##### WINGs Engineer’s Specification

# Part 1: General

A. The contractor shall furnish, install and place into operation comprehensive cellular/Wi-Fi and redundant cloud-based camera surveillance; laboratory microbiology AI analysis, and SCADA control system for the water treatment facilities as described herein. All equipment is to be completely factory assembled, wired and tested prior to shipment. The system shall	be WINGs ™ Series as manufactured by OmniSite, Inc

B. The name of manufacturers in this specification is not intended to eliminate competition or prohibit qualified manufacturers from offering equipment. Rather, the intent is to establish a standard of excellence for the material used, and to indicate a principle of operation desired. The base bid shall be the specified OmniSite equipment. Alternate proposed systems shall be submitted to the owner at least 14 days prior to bid (in accordance with the following pre-submittal requirements). Acceptable alternate equipment is listed below:

- Allen Bradley

- Group Schneider

- VTSCADA by Trihedral

- Primex

- USEMCO

C. Not less than (100%) of all equipment shall be standard catalogued products of the telemetry system supplier to assure one source responsibility, proper system interconnections and reliable, long-term operation. The telemetry supplier shall provide all control equipment and employ full-time engineering, service and support personnel necessary to provide and support the complete system.

# 1.03 System Coordination and Single Source Responsibility

A. The equipment provided shall be a completely integrated, cellular, automatic surveillance, SCADA monitoring, AI based microbiology lab analysis, and control system consisting of the required power equipment (circuit breakers, transformers etc.), automation and alarm monitoring equipment in a factory wired and tested assembly. The automatic control and camera surveillance/monitoring/AI (artificial intelligence) system components shall be standard, cataloged, stocked products of the telemetry system supplier to assure one source responsibility, immediately available spare/replacement parts, proper system interconnections and reliable long-term operation. The entire system software will be fully configured by the owner, using a simple fill-in-the-blank configuration method. Systems that require trained programmers, or factory software setup and configuration for future software edits will not be acceptable.

1.04 Drawings

A. The complete assembly shall be provided with job-specific wiring diagrams, parts lists, enclosure dimensional and door layout drawings and instructions.

B. Shop Drawings shall be submitted for approval for all equipment herein specified. The Shop Drawing Submittal shall include a Document List. An Order Specification shall be included which shall describe in detail all equipment provided. Each panel shall be provided with job-specific wiring diagrams, parts list, enclosure door layout and enclosure dimension drawing. The wiring diagram requirement applies to all field mounted instruments, control and telemetry equipment as well as all required interfacing to the power panel. Interconnection details shall be shown for all field mounted instrumentation. A description of Operation shall be provided detailing the operation of the complete system, including telemetry, camera surveillance, lab analysis, control and alarm handling.

C. Provide Record Drawings and Instruction Manuals. These manuals shall include corrected Shop Drawings. In addition, a detailed Programming and Operations Manual for the Microprocessor-based Controller Unit shall be included. The manual shall include all information as detailed for the Shop Drawing Submittals above.

# 1.05 Pre-submittal Information Required for Alternate Manufacturers

A. Full description and performance data on all substitute items proposed with references or verification of performance for such equipment already in service shall be provided. The PREBID Qualification Submittal shall include the following:

B. A reference project list with a minimum of five (5) reference projects shall be included.

The referenced project list shall include the following information for each project listed; project name, a brief description of the project (to include number of locations, communications medium employed and any/all control loops), the name and telephone number for a contact person. All reference projects given shall be web-to-wireless, combination camera surveillance, microbiology lab service systems including internet-based configuration, Ethernet/IP PLC gateway interface, 3rd party OPC interface, redundant cloud hosting, local back-up pump control and monitoring and personnel identification similar in size and scope to this project.

C. Detailed description of how the proposed substitute differs from that specified including but not limited to materials of construction, fabrication, operation, warranty, service, communications technology, corrosion protection, power consumption and maintenance requirements. A detailed comparison of the Internet based interface plus camera surveillance and laboratory interface must include detailed specification comparisons, and a description of how the proposed system meets and/or exceeds the OmniSite technique

D. Detailed discussion of why the proposed substitute is equal or superior to that specified in material of construction, fabrication, operation, warranty, service, corrosion protection, power consumption and maintenance requirements.

E. Tracings and four copies of revised prints reflecting in detail any and all changes in arrangement for materials, equipment, piping, fabrication, erection, maintenance, power supply, etc.

F. Provide a Programming and Operations Manual for the Microprocessor-based controller.

The manual shall include the following information as a minimum:

1.	How to view and change between the various displays.

2.	Alarm displays and a list of alarms handled.

3.	Alarm handling (ISA sequence used, etc.).

4.	Status displays and a list of statuses handled.

5.	Status Handling

6.	Analog control setpoint adjustment and displays.

7.	Analog alarm setpoint adjustment and displays.

- Access code usage.

- Photographic imagery system setup, usage and maintenance

- Personnel tracking system description, logging technique and use

11.	An example of programming values.

12.	Use of the real-time calendar/clock, including changing the time and date.

13.	A table for entering the values programmed at the factory.

- A table for entering the values programmed in the field.

- Description of proposed web-based interface and security features

- Sample lab microscope interface and AI system operation

- Video alarm validation sequence

G. Name and telephone number of person (s) to contact to answer questions or supply additional information. No alternate manufacturers are exempt from pre-submittal requirements.

H. Name and telephone number of factories authorized local sales and service personnel. Local factory authorized sales and service personnel must be experienced with the equipment proposed. Provide documentation stating that the factory authorized sales and service personnel have not less than three (3) years experience with the equipment proposed.

I. Failure to name an approved manufacturer in each space provided in the proposal will constitute grounds for declaring the bid irregular, or if the Owner chooses, give the prerogative of equipment selection solely to the Owner. If more than one manufacturer is named in any space it will declare that the Bidder has not preference and will give the prerogative of equipment selection solely to the Owner.

J. The right is reserved to reject any and all proposals, to waive any informality, irregularity, mistake, error or omission in any proposals received and to accept proposal, as determined by the Engineer or Owner, deemed most favorable to the interests of the Owner.

Part 2: Scope

### 2.01 The Overall Camera Surveillance, Lab,  and Web Based Interface System Shall Perform the Following:

The OmniSite WINGs is optimized for advanced pump station control, IP camera surveillance, PLC gateway interface using Ethernet/IP protocol, Lab microscope analysis, general I/O monitoring, personnel identification, and ease of use. The completed system provides the following standard calculations, presented in a user-friendly graphical format, to be overlaid onto the client’s existing, private web-pages.

- Well(s) Level

- Well(s) level high and low alarms

- Personnel Identification station using PIN entry

- AI powered indicator organism identification and counts from a camera microscope

- Access to the Omnisite National microbe database

- Nationwide chat interface to allow lab operators to opt-in to sharing and discussion of microbe questions and plant operations

- Power Failure

- Well drawdown rate (using automatic timed well drawdown tests)

- Pump-1,2,3 amp draw

- Pump-1,2,3 on/off cycles

- Pump-1,2,3 runtime

- Pump-1,2,3 failure

- Rainfall (if connected to an external rain gauge)

- Video and audio alarm validation sent direct to user phones

- Daily Time stamps of when alarm events occurred, and who responded

- Cellular signal strength indication

- Alarm notification using e-mail, pager, or voice call

- Alarm validation method that includes 20 second camera video (10 sec before event, and 10 sec after event) that is sent to any number of operator’s phones on a triggered alarm event to verify the site conditions. This video includes audio, and operator can select “view live feed now” from phone app.

- Historical log showing all alarm history and continuous water levels, plus historical camera video tied to alarm events, and well sound vs GPM pumping profiles with standard deviation analysis

- Web-based graphs of historical data that can also be exported to Microsoft Word or Excel programs, or exported to 3rd part SCADA systems employing OPC interface standards

- Low back-up battery alarm, with rechargeable lead-acid battery, including onboard automated battery load test system. Products without an automated battery load test will not be considered

#### TO INCLUDE: (Each Remote Site)

1-Weatherproof 4X – 16” X 10” X 4” polycarbonate enclosure.

1- Operator Interface 5” full color LCD touch display with backlight

1-Surge Arrestor.

1-WINGs ™ Remote Telemetry Unit.

1-Power supply, charger, backup battery and filter.

1-WINGS 4G Cellular Modem, with Wifi, GPS, and Bluetooth

1-WINGs explosion proof well camera with heat sensor, and microphone

1- Set of slip-on pump amp probes

1-15VDC power supply

- High gain, multi-element phantom antenna for 4G, 4G diversity, Wifi, GPS

- WINGs laboratory camera microscope interface for AI analysis, and counting of indicator organisms, plus AI powered recommendations for plant adjustments for optimum wastewater treatment

Remote Site List – The above standard monitoring list at each remote site shall be accompanied by the following site specific alarm and/or monitoring I/O

1)  Engineer, please fill in the remote sites to be monitored and any additional I/O

2)

3)

4)

5)

6)

7)

8)

9)

10)

11)

12)

13)

14)

15)

DETAILED SYSTEM SEQUENCE OF OPERATION: (Each Remote Site)

Designer – In this area, include an exact sequence of operation that must occur in addition to any standard sequences listed above. If no additional interlocking or control is required, then this section can be deleted

Part 3: Products

### 3.01  	Microprocessor-Based WINGs™ Controller

A. A Microprocessor-based Controller Unit shall be provided for monitoring and control of the pump stations based on alarm contact closures, universal voltage input signals, 4-20mA signals, cameras, PLC gateway interface using Ethernet/IP protocol, and relay outputs.

B. The Microprocessor-based monitor shall be a standard, catalogued product of a water and wastewater equipment manufacturer regularly engaged in the design and manufacture of such equipment. The pump/alarm monitor should be specifically designed for pumping automation utilizing standard hardware and software. “One of a kind” systems using custom software with a generic programmable controller, or pieces from many manufacturers that are “integrated” together will not be acceptable. The controller shall be WINGs ™ as mfg. by OmniSite, Inc.

C. The controller shall accept (8) universal DI configurable to monitor dry contacts or any voltage range between 12VDC/VAC to 120 VAC/VDC with two(2) of these inputs convertible to act as pulse counters; (5) 4-20mA isolated analog inputs, , (1) 20 amp relay output, (1)rain gauge input, and (1) crew on-site touchscreen PIN code input in its base form, (2) ethernet ports on dual NICs, (2) USB ports, (1) SD card slot to act as camera DVR, GPS location, and wifi communications with 4G cellular fall back.  It shall have Wago type removable terminal blocks.

D. Gel Cell Battery: On-board 12VDC, 1800mAH AGM battery provides backup for up to 12 hours in the event of power loss. Battery is automatically recharged using temperature compensated floating battery charging circuit and includes automatic battery load testing circuitry. Cellular transmitters such as the WINGs device will not transmit during AC power loss conditions without a known, working back-up battery. For this reason, any alternate products that do not include an automated battery load testing circuit will not be considered. The backup battery small includes a thermostatically controlled low watt density heater to keep the battery, touchscreen, and overall electronics operational at -15 degf

E. One 20-amp Control Relay: Heavy duty 20-amp control relay is used to control up to any number of pumps by connecting it to a sequencing or alternation relay. pumps and one alarm light/horn based upon water level and includes automatic pump alternation. Pump control relays shall have adjustable control direction, set points, and dead bands. A dedicated “level simulation button” is used to manually activate relays and determine proper operation. Inter-start time delays shall be utilized to prevent “slamming-on” all pumps together after a power failure. A dedicated “override” key on the user keypad shall allow simple removal of a pump from automatic control when “out of service”. A third dedicated “level setpoint” key allows simple adjustment of on/off setpoints without the need for laptop computers or complex re-programming

F. LCD display: 5” diag full color, high visibility, back-lit touch screen is viewable in very bright sunlight, total darkness or very high or low temperatures. This high visibility operator display is used to configure and monitor variables and eliminates the need for programming devices such as laptop computers. Includes built-in screen saver that continuously scrolls values of all inputs and calculations for easy viewing and setpoint adjustment. Color touchscreen implements a “real time database” feature, where all variables entered to any WINGs device is automatically recorded and backed-up at the Omnisite backend website, and conversely, and changes made at the Omnisite cloud backend are automatically downloaded to the WINGs device. This is done to ensure all databases are always in synchronization, and systems not employing this feature will NOT be considered

G.	Dual NIC ethernet ports: Ethernet port 1 is dedicated to have the ability to connect to a 5 port ethernet switch and monitor up to (4) Ethernet IP cameras. One camera is dedicated to monitoring the wet well, and others can be above ground for any monitoring applications. The 2nd ethernet port is dedicated for connection to a PLC or any device that communicates via ethernet/IP. This port can communicate to a device in a R/W configuration up to 256 variables in a suitable device. Variables from an ethernet/IP device can also be used to trigger a camera alarm validation video recording AND be used in a peer-to-peer communications configuration where any PLC variable can be R/W to any other connected PLC or device, for a true peer-to-peer topography.

H. SD Memory card slot: Trend log data from connected variables, or video from cameras, shall  be stored on the memory stick for later retrieval. Memory shall have the ability to be used for updates to the RTU operating system eliminating the need for field laptop computers to repair operating program errors. Memory sticks are available from 32MB to 1GB.

I. Intelligent Camera Surveillance: WINGs rapid installation kit is supplied with standard well camera. Submersion, and explosion rated, with internal microphone to plot well sound vs. pumping rate for early detection of pump wear from bearings, cavitation, or being dislodged from rails and other issues. Trend log data from connected variables shall be stored in the redundant Amazon and Google clouds for backup and analysis.

J. On-Board I/O for backup to PLC Interface: The back-up I/O on the WINGs device can be directly wired to function in a stand-alone mode, using its’ local I/O and camera for equipment monitoring, or can be wired to function as “back-up” I/O in the case where an IP connection is made to a PLC system, and the communication to the PLC would fail, for any reason. This back-up I/O will continue functioning and monitoring, including the camera video, and video alarm validation sequences, even if the PLC interface is not operational. The onboard, back-up I/O includes (8) universal voltage digital inputs, (5) 4-20mA analog inputs, and (1) relay output.

K. Auto-roam, multi-carrier SIM card: The WINGs device will include a multi-carrier SIM card that can seamlessly auto-roam from Verizon to AT&T to T-Mobile, without operator intervention, such that if one carrier was non-functional, or a stronger signal is available on a different carrier, that signal can be used to improve transmit and receive reception

L. Peer-to-Peer Control: The WINGs product includes true peer-to-peer control that is configured using a simple, fill-in-the blanks control table. A system which includes complex radio and PLC custom programming will not be considered. The simple peer-to-peer table entry allows any operator to use a selected analog or digital from any OmniSite device to trigger an on/off control event at another OmniSite device. This can be used to interlock lift stations, or for water tower control schemes which include advanced alternation and grouping, as needed, to achieve complex control using OmniSite’s simple event-based-actions table entries

M. OmniAdvantage Emergency Stock Plan: Optional OmniAdvantage Plan includes a continuous 24/7 parts warranty and includes one emergency stock unit at the owner’s location to minimize downtime. If a WINGs device would fail for any reason, the spare, emergency stock unit, replaces the failed unit, the failed unit is returned to OmniSite for repair or replacement, as needed, and the new or reconditioned unit is placed back in the customer’s stock. This program ensures the maximum amount of “up-time” as the over-the-air programming ability of the WINGs device allows the emergency replacement unit, to receive the settings from the removed unit, using a one-click update method, to minimize complexity and downtime. Systems that require laptop computers, custom programming and cables, and specialized knowledge, will not be considered

N. Free Lifetime Technical Support: For as long as the customer owns the WINGs device, and the device is active on their account, the WINGs device and software include 24/7 free OmniSite technical support

O. Free Lifetime User Training: For as long as the customer owns the WINGs device, and the device is active on their account, the WINGs device and software include 24/7 free OmniSite personnel training at the OmniSite factory in Indianapolis, Indiana. This is a 1.5-day, full hands-on training course, and is available for any number of people, not to exceed 20. Customers are responsible for travel and lodging during training. OmniSite will provide food and training materials. No more than (4) training attendees per session

P. Fixed Monthly prices for wireless communications and Hosting: The OmniSite WINGs device includes FIXED, predictable monthly fees for back-end hosting and wireless services. Systems which do not offer fixed, predictable fees will not be considered

Q. Seamless radio upgrade plan: OmniSite has been the leader in wireless telemetry since 1999, and as such, has seamless radio upgrade plans for cellular radios as radio technologies are retired. For example, when the US 4G networks are retired, OmniSite will supply the customer with a socket-modem which can be used to replace the existing socket-radio modem. The customer simply removes the existing modem, and re-sockets the new modem. The WINGs device will automatically identify the radio replacement, will connect to the OmniSite server, and automatically update any/all software/firmware to seamlessly transition from 4G to 5G service. This same sequence applies as the device changes from 5G to 6G and so forth. This process, combined with OmniSite’s OTA firmware updates creates a “living product” where new software and radio features are made available to all WINGs devices such that it does not become obsolete, and gets new features across time, as opposed to just becoming outdated.

#### 3.02 Multimodal Color Graphic Software and Web-to-Wireless Technology

The Omni-site WINGs™ RTU is completely, programmed, setup, and configured using a standard web browser at the www.omnisite.com  website. All connected equipment can be monitored and configured from anywhere in the world using the worldwide Web. WINGs is a true multimodal product, analyzing camera video, still images, audio, camera microscope images, and traditional analog and digital sensor data, plus variables from PLC’s and any other devices capable of communicating via Ethernet/IP protocol

Proprietary programming software or skills are not required. Systems that require proprietary programming software, or cryptic interfaces will not be considered. Another significant feature of the WINGs is its ability to be positioned anywhere in the US, Canada, or Mexico without coordination with the local telephone company. There are no long-distance telephone charges for equipment located anywhere in the USA. This is a significant feature required by the client allowing them nationwide monitoring capabilities without long-distance telephone charges. Since WINGs is wireless it can be repositioned by the client at any time in the future without coordination with the telephone company (making it a truly mobile device), and monthly wireless fees are FIXED. Cellular systems that do not provide FIXED monthly fees or incur long distance charges for out-of-state calls will not be considered.

Additionally, the system described herein shall, at no future time, require the addition of radio repeaters, system software re-configuration, or installation of hard-wired telephone lines if a future remote site is added to the network. A future device shall merely “auto-populate” the clients existing data screens eliminating the need for specialized engineering and software creation.

The system software shall provide the following features:

- Upon Alarm condition: facilitate the compilation and transmission of alarm information plus a 20 second video and audio snippet to validate the event, to any brand of smartphone.

- Upon Alarm condition: facilitate the compilation and transmission of alarm/video information to commercially available PCs or tablets connected to the Internet.

- Upon Alarm condition: facilitate the compilation and transmission of alarm/video information to via email, text message, and voice call to user configurable call lists, based on time of day, and day of week, supporting multiple different work shifts.

- Allows for Voice Dial-in Connection via telephone line to facilitate the Acknowledgment of active alarms, or via iPhone or Android phone apps

- Allows Voice Dial-in Connection via telephone line, or via phone app, to facilitate the inquiry of values of digital and analog tags.

- Both Voice Dial-in and Voice Dial-out, plus phone app, access modes shall be protected by mandatory redundant password entry system.

- The OmniSite software supplies the unique ability of text-to-speech conversion of typed-in alarm messages so that sound files do not have to be manually recorded. This saves much time and programming complexity. Systems that do not employ advanced text-to-speech conversion will not be considered.

- Shall allow for the configuration and maintenance of a set of "global" voice data files used in the construction of voice output messages.

- This shall allow for the creation and maintenance of a "phone book" of destinations for alarm transmissions. The quantity of eligibility entries in the phone book shall be unlimited.

- We will have the ability to archive collected data and export this data to common Microsoft packages.

- This shall provide for the creation of "Groups" consisting of selected entries from the Phone Book. A "Group" may be a logical grouping of alarms, based upon the type of transmission desired as a result of any alarm condition. Group configuration shall allow for:

- Allow for selection of recipient list for alarm transmissions along with recipient priority determination.

- Allow for creation of user configurable delays prior to commencement of alarm transmissions.

- Allow for user selection of "single pass" or "continuous loop" modes through recipient list until alarms are acknowledged.

- Allow for user enable/disable of data logging to disk file, automatic acknowledgment upon return to normal of alarm condition, mandatory user acknowledgment of alarms.

- Shall provide for Digital Alarm handling and allow a textual description field and voice verbalization files for each Digital and analog Alarm. Standard alarm acknowledgment requires personal involvement.

- Shall allow for the creation and maintenance of "reports" or organized collections of tags. Such reports may be Voice accessed via telephone line employing a mandatory password protection system. The report’s feature shall make it possible to inquire and receive a verbalization 	of the description of the tag requested, along with the current value. This alteration process calls for the pre-configuration of the tag, making it available for inquiry and/or change.

- Execution Software

  - Shall be capable of displaying on screen, current alarm status and alarm history status of a minimum of 1,000,000 simultaneous alarm tags.

  - Shall allow for manual transmission of user entered notification lists via email, text, and voice call, by selecting destination from the phone book and message entry.

  - Shall be capable of maintaining a group-by-group activity log which may capture: Any alarms	that may occur (along with user configurable time and date stamp), any return to normal transactions, any voice dial-outs, any voice-dial-ins (including who has accessed the system and who has acknowledged alarms).

  - Historical data collection of all alarm events, alarm acknowledgements, and return-to-normal events. Line and bar graphs are used to present level and control data in a user-friendly format and can be exported at any time to other 3rd party software packages

  - No other special hardware or software is required for system operation.

- OmniSite Lab Services & National Microbe Database: The OmniSite software can be connected to a camera microscope which has connection to a local PC in the lab. This PC must have internet access to allow upload of microscope images and video to the OmniSite website. The OmniSite website uses AI to identify and count indicator organisms and keep an accurate record of these images and video in a database, along with all other salient process readings. Process readings are manually inputted, as are camera microscope video files. The OmniSite AI software will advise on plant adjustments based on process readings combined with historical performance, and microbiology populations of different indicator organisms. There are over 250,000 identified microbes in municipal wastewater, and millions that are unidentified. OmniSite’s AI lab interface allows an operator, who may have many other facility responsibilities, the ability to understand the advanced microbiology that exists at a modern wastewater facility and then get quick and convenient feedback regarding how to make plant adjustments. The operator has the ability to “opt-in” and make their microscopic video and data a part of the OmniSite Microbe National database, where the operator can then online chat with other OmniSite municipal facility operators, on a National scale, to problem solve complex issues, and also make their database available to academic research facilities to study the effects of man-made substances on single cell organisms. As a single example, the effects of plastics ingestion on single cell organisms, and correlate that data to the local health outcomes of the local human populations who contribute wastewater to that facility.

- User Audit Trail- The WINGs device employs a “real time database” where changes made in the field, via phone, PC, or tablet, are all automatically synchronized such that a change in one location is automatically reflected in all locations. This protects the customer from outdated, or undocumented changes. The real time database of the WINGs device is automatically backed up in the cloud at redundant servers residing at both Google and Amazon AWS to true redundant, separate, advanced hosting facilities.

- PLC Communications Gateway: The WINGs device will communicate to PLCs and devices that employ Ethernet/IP protocol. Up to 256 tag variables of any type can be read/written by the WINGs device into the target device. Read variables can be used in peer-to-peer control schemes, or to trigger camera alarm validation sequences just like on-board WINGs local I/O such that a facility investment in existing PLC infrastructure is maintained, and can be web-enabled via this cloud gateway

- OPC Interface to 3rd Party SCADA Software: The OmniSite WINGs platform can expose data to 3rd party SCADA platforms via the OPC standard. Updates to these 3rd party platforms, themselves, are made by others, and not OmniSite. The WINGs platform provides the concept of the “redundant cloud” where the OmniSite cloud interface, with it’s notifications by email, text, and voice, plus camera and audio data, run in parallel with the 3rd part SCADA interface, such that if the 3rd party system is down, for any reason, the OmniSite system can seamlessly function as the primary or backup system to ensure uninterrupted data and alarm delivery.

- OmniSite Super View Dashboard: The WINGs online dashboard is a responsive webpage that auto-scales the pages to fit on a PC, tablet, or phone screen of different sizes. This allows the operators to use a consistent interface across all devices, and not learn, or download and support, different interfaces for different devices. The WINGs dashboard is a true multimodal experience combining traditional analog and digital sensor data with audio, video, and AI to provide advanced insights that a simple PLC, alone, cannot provide in an easy-to-maintain, or cost-effective way.

- 100% Over-the-Air (OTA) Updates: The WINGs device can OTA 100% of all system settings and firmware into the onboard SOM, programmable microcontrollers, and other programmable chips, plus the radio, such that it is always up to date with the latest code. Cellular radios today receive frequent OTA updates to keep them current as networks change. Systems which do not provide 100% OTA updates will not be considered.

- Redundant and Cyber-security hosting facility: The WINGs utilizes redundant and cybersecure clouds at both Amazon AWS and Google. OmniSite can supply an annual cybersecurity audit certificate verifying the status and condition of OmniSite’s overall cybersecurity plan. This audit is done by a 3rd party audit firm as recommended by Google and AWS and is not done by OmniSite.

- Intelligent PIN code: Intelligent PIN code identifies operator on site and logs who visited site, took equipment out of service, etc. PINs can be reprogrammed by color touchscreen on site, or at the OmniSite website if an operator has correct security credentials, eliminating the need to contact the factory for PIN re-programming.

### 3.03 Incoming Service and Lightning Arrestor

A. The incoming service for the control system shall be 120-volt, 1 phase, 3 wire, 60 Hertz. A single-phase lightning arrestor shall be supplied in the control system and connected to each line of the incoming side of the power input terminals. The arrestor shall protect the control system against damage as the result of transient voltage surges caused by lightning interference, switching loads and power line interferences. It shall begin shunting to ground at 500 volts maximum.

B. All metering shall be done ahead of the main disconnect and control panel. The meter shall be supplied and installed by the Contractor in accordance with local power company requirements.

C. The electrical service shall be provided by the utility. Electric meter base shall be provided by the owner and installed in accordance with the requirements of the electric utility. A UL rated main disconnect switch, circuit breaker panel, conduit and wiring between the power company termination and the control panel shall be furnished and installed by the contractor. The power supply to the control panels shall be 120 volts, one phase, three wire, 60 Hertz.

### 3.04 15 VDC Power Supply

A. A regulated 15 VDC power supply shall be provided for the WINGs device, and other monitoring system components, as required. The power supply shall include a terminal block for incoming AC. The power supply shall be powered from a 120 VAC and include tapered charge type battery charging circuitry to maximize battery life. The power supply shall be rated at minimum of 2.0A @ 15 VDC.

B. The power supply system shall include (1) 12 Volt battery sized to allow for 12 hours continued system operation during a power outage.

C. The WINGs™ power supply contains a fuse-protected, internal loop power supply capable of providing loop power for up to (5) external 4-20mA, 2-wire loop powered devices, and (2) IP cameras.

### 3.05 Signal Transient Protection

A. Transient protection shall be provided with all equipment to protect all instrumentation and telemetry devices either receiving or sending signals.

B. The transient protectors shall be 4000V optical isolators which shall effectively arrest most transients encountered in an instrumentation environment.

### 3.06 Enclosure

A. NEMA 4X polycarbonate 16 X 10 X 4”. Includes stainless pad-lockable hasp(s)

### 3.07 Antennas

A. The antenna for each location shall be selected based on the results of the cellular survey.

B. All antennas shall be provided and installed by the telemetry contractor as per recommendations from the manufacturer.

1.	The Systems supplier shall be responsible for installation, set-up, adjustment and tuning of the antenna to provide optimal communications for the system.

2.	The antenna installation shall be external to the enclosure and shall be outdoors.

3.	The Systems supplier shall utilize the WINGs™ built-in Radio Frequency signal meter during antenna installation to ensure that the antenna is installed for optimum signal reception.

C. The Contractor shall ensure that the cellular Network system work is properly interfaced with equipment and other work not furnished by the Systems supplier.

D. The Systems supplier shall install, make final connections to, adjust, test, and start-up the complete cellular Radio Network.

# Part 4: 	General Equipment Requirements

4.01		Wiring

A. All wiring shall be minimum 600-volt UL type MTW or AWM and have a current-carrying capacity of not less than 125% of the full load current. The conductors shall be in complete conformity with the national electric codes, state, local and NEMA electrical standards. For ease of servicing and maintenance, all wiring shall be color coded. The wire color code shall be clearly shown on the drawings, with each wire’s color indicated.

B. All control wiring shall be contained within plastic/PVC wiring duct covers. Where dimensional constraints prevent the use of wiring duct, wires shall be trained to panel components in groupings. The wire groupings shall be bundled and tied not less than every 3 inches with nylon self-locking cable ties as manufactured by Panduit or equal.

C. Every other cable tie shall be fastened to the enclosure door or inner device panel with a cable tie mounting plate with pressure tape. Where wiring crosses hinged areas such as when trained from the inner device panel to the enclosure door, spiral wrap shall be used.

D. The installation of the equipment described herein is provided by the electrical contractor in accordance with the electrical specification section of this project, and according to the detailed project drawings. Final equipment test, supervision and certification supplied by Omni-site trained representative.

4.02		NAMEPLATES

A. All major components and sub-assemblies shall be identified as to function with laminated,    nameplates.

Part 5: Execution

#### 5.01		Field Installation

A. The services of a factory trained, qualified representative shall be provided to certify the completed system, make all adjustments necessary to place the system in trouble-free operation and instruct the operating personnel in the proper care and operation of the equipment.

#### 5.02		Guarantee

A. All equipment shall be guaranteed against detects in material and workmanship for a period of one year from the date of Owner’s final inspection and acceptance to the effect that any defective equipment shall be repaired or replaced without cost or obligation to the Owner.

06/14/95